Temperature PID Control
A practical approach using Ziegler-Nichols
Caramon Pi
Håkan Brolin, 2017-02-27

---
Closed Loop System
PID algorithm
Discrete form
Improved controller, by basing the derivative term on the process value only

---
Ziegler-Nichols
	Kp	Ti	Td
P	Ku / 2	-	-
PI	Ku / 2.2	Pu / 1.2	-
PID	Ku / 1.7	Pu / 2	Pu / 8
Closed-loop tuning method
Ulitmate gain, Ku=360
Ultimate period, Pu=35 minutes = 2100 sec
Sample time, Ts = 10 minutes = 600 sec (*)
(*) Values measured 2016 using CMON R1Axx

---
Controller Parameters
Ku	360
Pu [s]	2100
Ts [s]	60
	Kp	Ti [s]	Td [s]
P	180.00	-	-
PI	163.64	1750	-
PID	211.76	1050	262.50
Z-N
Sample time decreased from 600s to 60s.
Possible due to new hardware with SSR.
Ki = (Kp x Ts) / Ti
Kd = (Kp x Td) / Ts
	Kp	Ki	Kd	Comment
PID-1	163.64	5.61	-	Z-N, PI
PID-2	211.76	12.10	926.45	Z-N, PID
PID-3	163.64	28.05	-	PID from CMON R1Axx

---
Step-up
Kp=163.64, Ki=28.05, Kd=0.00
Step-up
Kp=211.76, Ki=12.10, Kd=926.45

---
Step-down
Kp=163.64, Ki=28.05, Kd=0.00
Step-down
Kp=211.76, Ki=12.10, Kd=926.45

---
Conclusions
- PID-2 is a “true” ZN PID using Ts=60s.
- PID-3 was derived 2016 using Ts=600s.
  Not fitted for the new hardware using SSR and with less Ts.
  Is a PI and not PID.
- PID-2 has less overshot compared to PID-3.
- PID-2 settles faster than PID-3.
- PID-2 seems less “aggressive” on step-up.
- Both PIDs perform well on step-down.
- The slower decrease of temperature on step-down for PID-2 can be explained by the fact that outdoor temperature was higher during this experiment.
- Some questions can be raised about using the old values for Ku and Pu, as they were derived using Ts=600s. It could be necessary to perform new
  experiments using the new hardware with Ts=60s.